## Slide 1: EE 521/ECE 582 – Analysis of Power systems
Class #5 – September 8, 2022
Dr. Noel N. Schulz
Edmund O. Schweitzer III Chair in
Power Apparatus and Systems
Chief Scientist Joint Appointment, PNNL
Co-Director, PNNL/WSU Advanced Grid Institute (AGI)
Washington State University Pullman
Noel.Schulz@wsu.edu EME 35
509-335-0980 (o) and 509-336-5522 (c)

## Slide 2
Here are my office hours via zoom and in-person as possible. I will let you know when I am in each location
Tuesdays 4:30-5:30 pm (after class)
Wednesdays 4-5 pm
Fridays 1:30-2:30 pm
Below is the zoom information for the semester! I will also set other times to go over your code individually.
Join from PC, Mac, Linux, iOS, or Android: https://wsu.zoom.us/j/8237216735 (Links to an external site.)
Meeting ID: 823 721 6735

## Slide 3: Programming Projects: (80%)
Power Flow Project (20%)
  Ybus, Jacobian matrices – Newton Raphson
  LU Factorization, Backward-Forward substitution for NR
  Fast Decoupled
  Q-limits, transformer taps
Using IEEE 14 bus system as given, and I will provide a slightly modified version after you confirm the 14-bus system.
Projects build on each other, adding different features
In addition to getting the right answers, for each program we’ll set up a session for you to describe your code to me.
Copying code from a colleague or from on-line resources is not permitted.

## Slide 4: Newton-Raphson and Parts
Output Results
Input Data
Calculate Ybus
Calculate Jacobian Terms
Iterative Solution
Output Results
Calculate Jacobian Terms
Solve Equation [A][x] = [b]
Check Mismatch?
Calculate Mismatch]
Small enough

## Slide 5: Solving the Matrix once you calculate it
An elementary row operation is one of the following:
  Interchange any two rows of the matrix
  Multiply any row by a constant
  Take a linear combination of rows and add it to another row

## Slide 6
Gaussian Elimination for solving Ax=b
is the process of using a series of elementary row operations to convert:
An elementary row operation is one of the following:
  Interchange any two rows of the matrix
  Multiply any row by a constant
  Take a linear combination of rows and add it to another row
solution
Identity matrix

## Slide 7
Upper Triangularize (i.e. zero out all elements below the diagonal) using elementary row operations (EROs)
Then back substitute to find solutions
(EROs)
All zeros below diagonal
Basic Approach to Gaussian Elimination

## Slide 8
ERO(4)
Scale diagonal a11 to 1
(in this case ERO(4) = identity since a11 is already 1)
Update A by EROs 1 through 4
A
ERO(2)
ERO(3)
ERO(4)
ERO(1)
A’
All zeros

## Slide 9
Update A’ by EROs 5 through 7
A’
ERO(5)
ERO(6)
ERO(7)
A’’
All zeros
Now eliminate third column
ERO(8)
And diagonalize
ERO(9)
A’’’

## Slide 10
Normalize to 1
ERO(10)
A’’’
Multiply b by EROs 1 through 10:
ERO(10)ERO(9)ERO(8)…ERO(1)b = b’’’’ =

## Slide 11
Now we can use back substitution to find x1, x2, x3, and x4
x*

## Slide 12
LU Factorization is an extension of Gaussian elimination in that the forward triangularization process is formalized such that the matrix A is factorized into an upper triangular matrix (U) and a lower triangular matrix (L) such that
So how does this help us solve Ax=b?
LU Factorization

## Slide 13
Note that Ax=b implies that LUx=b. If we introduce a “dummy” variable y such that y=Ux, then
Since L is lower triangular, then it is easy to solve for y!
And once we have y, then we can solve Ux=y, where U is upper triangular.
This is forward substitution.
This is backward substitution.

## Slide 14
Let
L
U
Note that U has ones (1) on the diagonal
Q will be calculated first by column and then by row
Q =

## Slide 15
Initialize Q to the zero matrix. Let j=1.
Complete the jth column of Q (jth column of L) as
If j=n, then stop.
Assuming that qjj  0, complete the jth row of Q (jth row of U) as
Set j=j+1. Go to step 2.
Note that Q overwrites A, thus they can both be stored in the same matrix!
Crout’s algorithm for computing LU from A

## Slide 16
Example: To find q55:

## Slide 17
Similarly: To find q65:

## Slide 18
Example: Find the LU factors of the A matrix
Let j=1, then from we get and the first column of Q is just the first column of A:
For the first row of Q, we use
from which
3
4
8

## Slide 19
Second column ( j = 2):
q22 = a22-q21q12 = 1-(2)(3) = -5
q32 = a32-q31q12 = 3-(4)(3) = -9
q42 = a42-q41q12 = 2-(9)(3) = -25
Second row:

## Slide 20
Third column ( j = 3):
Third row:

## Slide 21
Fourth column ( j = 4)
Check: LU=A?


## Slide 22
Solve
Solve Ly = b using Forward substitution
Note that this is exactly the same backward substitution that we had for Gaussian Elimination!
2. Solve Ux=y using Backward substitution

## Slide 24: Challenges Solving Problems with Computers
Numerical things to think about when solving on the computer
What is zero?
What is good enough when solving?
Now do the magnitude relationships affect our results?

## Slide 25
Partial Pivoting for LU factorization
Solve
We can estimate that the solution to this system will be:
Find LU factors:

## Slide 26
Solve for y:
Solve for x:
This cannot be correct!
It should be x1  2
What happened?

## Slide 27
The problem is that 10-10 is too close to zero for most computers (and human) accuracy, essentially leading to a “divide by zero” problem
We can fix this error by rearranging the equations:
The LU factors are:
Resulting in:
Then:
Much better!

## Slide 28
We can introduce a pivoting strategy to move the largest element to the diagonal to avoid any potential divide by zero problems
Partial Pivoting Strategy
At the jth step of the LU factorization, choose the kth row as the exchange row such that
Exchange rows and update A, P, and Q correspondingly
What is P?

## Slide 29
P is a permutation matrix that reflects any row interchanges that have occurred during partial pivoting. P starts as the identity matrix.
Swap rows

## Slide 30
Repeat previous example with partial pivoting.
This is the largest element in the first column.
Swap row 1 and 4
Calculate first column of Q
Calculate first row and second column of Q
This is the largest element in the second column.
Swap row 2 and 4
Calculate second row and third column of Q
This is the largest element in the third column, so no pivot required.
Calculate third row and fourth column of Q

## Slide 31
How is P used?
Start with
Premultiply both sides by P :
Substitute:
Solve:
This is just a reordered b vector
Then: (same as usual. The order of x remains unchanged.)

## Slide 32
Complete Pivoting for LU factorization
In some cases, complete pivoting is used in which the largest element remaining (rather than in just the column) is pivoted to the diagonal element.
This requires both a column and row pivot.
In this case, two permutation matrices are developed such that
Solve for z, then x = P2 z.
The vector z has the same values as x, just in a different order.
The action P2z reorders the values back to the original order.
Then (as before)
Now define P2 z = x, then

## Slide 33
Initialize Q to the zero matrix. Let j=1.
Complete the jth column of Q (jth column of L) to the jth column of the reduced matrix A(j), where A(1)=A and
If j=n, then stop.
Assuming that qjj  0, set the jth row of Q (jth row of U) as
Update A(j+1) from A(j) as:
Set j=j+1. Go to 2.
Gauss’ algorithm for computing LU from A

## Slide 34
Stationary Iterative methods for solving Ax=b:
Iterative methods generate a sequence of approximations to x* from an initial guess (i.e. x0, x1, x2, … xk ) such that xk  x* as k  .
If convergent1, these methods are accurate to within a user-defined convergence criterion.
Examples include:
Gauss Jacobi
Gauss Seidel
Successive Over-Relaxation
1 we’ll discuss convergence later

## Slide 35
Relaxation methods for solving Ax=b:
Start with Ax = b
Define a matrix M such that:
Rearranging:
Adding iteration indices:
The choice of M determines if, and how fast, Ax – b  0.
When , for some small , then the iteration is said to have converged.

## Slide 36
Jacobi
Let M = D (the diagonal elements of A), then
Or in scalar form:
This method is attractive for parallel processing applications because each depends only previous values of xk. Thus each ith element can be calculated independently.

## Slide 37
Solve using the Jacobi method.
Set up the equations:

## Slide 38
-1.1978
-0.8026
-1.0258
-1.0494
Jacobi

## Slide 40
Solve using the Gauss-Seidel method.
Set up the equations:

## Slide 41
Gauss-Seidel
-1.1978
-0.8026
-1.0258
-1.0494

## Slide 42
Gauss-Seidel
Jacobi

## Slide 43
The Gauss Seidel method took fewer iterations to converge than did the Gauss Jacobi method.
Is it possible to predict if, and how fast, a method may converge?
Consider the matrices MJ and MGS. If all of the eigenvalues of MJ or MGS lie within the unit circle in the complex plane, then the iteration will converge for any initial guess.

## Slide 44
eig(MJ)=
Convergence guaranteed!
eig(MGS)=
Convergence guaranteed!

## Slide 45
Consider now the Jacobi method applied to the following system of equations:
(used previously in LU factorization example)

## Slide 46
Iterations will not converge
Not converging!

## Slide 47
Successive Overrelaxation
The Gauss-Seidel iteration
can be rewritten as:
Upper triangular part of A
(not the U from LU factorization)
Add a weighting factor 0 <  < 2:
If  = 1, then the method reduces to the Gauss-Seidel.
For large systems, this method can potentially converge much more rapidly than
either Jacobi or Gauss-Seidel, but it is difficult to find an optimal value of 

## Slide 48: Newton-Raphson and Parts
Output Results
Input Data
Calculate Ybus
Calculate Jacobian Terms
Iterative Solution
Output Results
Calculate Jacobian Terms
Solve Equation [A][x] = [b]
Check Mismatch?
Calculate Mismatch]
Small enough
L-U Factorization
Backward/ Forward Substitution

## Slide 49: Programming Projects: (80%)
Power Flow Project (20%)
  Ybus, Jacobian matrices – Newton Raphson
  LU Factorization, Backward-Forward substitution for NR
  Fast Decoupled
  Q-limits, transformer taps
Using IEEE 14 bus system as given, and I will provide a slightly modified version after you confirm the 14-bus system.
Projects build on each other, adding different features
In addition to getting the right answers, for each program we’ll set up a session for you to describe your code to me.
Copying code from a colleague or from on-line resources is not permitted.

## Slide 50: Reminder
Here are my office hours via zoom and in-person as possible. I will let you know when I am in each location
Tuesdays 4:30-5:30 pm (after class)
Wednesdays 4-5 pm
Fridays 1:30-2:30 pm
Below is the zoom information for the semester! I will also set other times to go over your code individually.
Join from PC, Mac, Linux, iOS, or Android: https://wsu.zoom.us/j/8237216735 (Links to an external site.)
Meeting ID: 823 721 6735

## Slide 51: Announcements
Review examples from Chapter 2
Read Sections 3.1 and 3.2
Working on MATLAB Program
  Input the CDF file – Start with Data in Program
  Start working on building the Ybus
  Calculate Jacobian Matrix Values
  Work on LU Decomposition